74:56:01:15.  Operation and maintenance of cathodic protection -- Criteria for taking tests. One or more of the following criteria must be met when taking tests of UST systems:

(1)  A negative potential of at least 0.85 volts (V) measured between the UST system and a saturated copper sulfate (Cu2SO4) reference electrode touching the soil above the tank;

(2)  A negative shift in potential of at least 300 millivolts (mV) (.30V) as measured between the UST system and the copper sulfate electrode. This shift is the difference between the unprotected potential and the potential with the impressed current applied;

(3)  A negative polarization potential shift of at least 100 millivolts (mV) (.10V) as measured between the UST system and the copper sulfate reference electrode contacting the soil. This shift is the polarization decay determined after the protective current is disconnected; or

(4)  Other criteria that demonstrate proper levels of corrosion protection, as approved by the department.

Voltage measurements (IR drops) other than those across the electrolyte boundary of the structure are considered valid voltage measurements taken for the criteria in subdivision (1) to (3), inclusive, of this section.

Owners or operators of all new and upgraded UST systems shall certify compliance with corrosion protection requirements on the certification of compliance form in accordance with § 74:56:01:12.

Source: 14 SDR 76, effective November 29, 1987; transferred from § 74:03:28:06, 18 SDR 62, effective October 10, 1991; transferred from § 74:03:28:06.01, July 1, 1996; 23 SDR 131, effective February 24, 1997.

General Authority: SDCL 34A-2-93, 34A-2-99.

Law Implemented: SDCL 34A-2-98, 34A-2-99.