44:73:12:45.  Detached structures. A detached structure or auxiliary building used for combustible storage or vehicle parking built adjacent to, but not directly attached to, a health care facility shall either be separated from the facility by a minimum distance of 20 feet, provided with two-hour fire rated separation, or equip the structure with a complete automatic sprinkler system.

Source: 15 SDR 155, effective April 20, 1989; 22 SDR 70, effective November 19, 1995; transferred from § 44:04:13:49, 42 SDR 51, effective October 13, 2015.

General Authority: SDCL 34-12-13(1)(3).

Law Implemented: SDCL 34-12-13(1)(3).

Cross-Reference: Fire safety code requirements, § 44:73:03:01.